## Details
Table 1b. Development Information.
Development | River Name | Nearest Town, County, State | River Mile of Dam | Dam Latitude | Dam Longitude | Date of Initial Operation | Total Installed Capacity (MW) | 2010-2019 Average Annual Generation (MWh) | Mode of Operation | Number, type, and size of turbines | Minimum Hydraulic Capacity (CFS) | Maximum Hydraulic Capacity (CFS) | Trashrack clear spacing (inches), for each trashrack | Dates and types of major equipment upgrades | Dates, purpose, and type of any recent operational changes | Plans, authorization, and regulatory activities for any facility upgrades or license or exemption amendments | Date of original construction and description and dates of subsequent dam or diversion structure modifications | Dam or diversion structure height including separately, the height of any flashboards, inflatable dams, etc. | Spillway elevation and hydraulic capacity | Tailwater elevation (provide normal range if available) | Length and type of all penstocks and water conveyance structures between the impoundment and powerhouse | Dates and types of major infrastructure changes | Designated facility purposes (e.g., power, navigation, flood control, water supply, etc.) | Source water | Receiving water and location of discharge | Date of conduit construction and primary purpose of conduit | Authorized maximum and minimum water surface elevations | Normal operating elevations and normal fluctuation range | Gross storage volume and surface area at full pool | Usable storage volume and surface area | Describe requirements related to impoundment inflow, outflow, up/down ramping and refill rate restrictions. | Upstream dams by name, ownership and river mile. If FERC licensed or exempt, please provide FERC Project number of these dams. Indicate which upstream dams have downstream fish passage. | Downstream dams by name, ownership, river mile and FERC number if FERC licensed or exempt. Indicate which downstream dams have upstream fish passage | Operating agreements with upstream or downstream facilities that affect water availability and facility operation | Area of land (acres) and area of water (acres) inside FERC project boundary or under facility control. | 2010-2019 Average annual flow at the dam | 2010-2019 Average monthly flows | Location and name of closest stream gauging stations above and below the facility | Watershed area at the dam (in square miles). Identify if this value is prorated and provide the basis for proration. | Number of zones of effect | Upstream and downstream locations by river miles | Type of waterbody (river, impoundment, bypassed reach, etc.) | Delimiting structures or features | Designated uses by state water quality agency
Somerset | Deerfield | Somerset, Windham, VT | 66 | 42°58'25.76"N | 72°57'1.10"W | N/A | N/A | N/A | Seasonal storage | N/A | N/A | N/A | N/A | No major equipment upgrades have taken place since the previous LIHI submittal | Loon nesting target elevation changed on May 18, 2017. See Page 2 of report. | No facility upgrades or license amendments are planned | 1913 | 110' | 2133.58' - 6,470 cfs at 2139.58' | Dam - 2035' to 2038' | N/A | No major infrastructure changes have taken place since the previous LIHI submittal | Storage | Deerfield River | Deerfield River | N/A | Aug 1 to Nov 1: 2120' Nov 2 to Apr 30: 2107' May 15 to Jul 31 or notification that loon nesting is complete or will not occur: Target elevation - 2128.23' and maintained +/-3" | 2125.0' - 2130.0' | 57,345 AF 1,514 AC | 20,614 AF 970 AC | Oct 1 to Dec 15: Minimum flow - 30 cfs Dec 16 to Feb 28: Minimum flow - 48 cfs Mar 1 to Apr 30: Minimum flow - 30 cfs May 1 to Jul 31: Minimum flow - 12 cfs or inflow but not less than 9 cfs Aug 1 to Sep 30: 12 cfs Maximum discharge - 312 cfs, or instantaneous inflow if higher (except during Loon season) Ramping Restrictions (Aug 1 – Apr 30): Upramping at 100 cfs or less over 24 hours Downramping at 50 cfs or less over 24 hours Loon protection: Attain a target elevation of 2128.23 feet msl by May 15 and manage the level to stay within a range of +/- 3 inches of the target elevation through July 31. | N/A | Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. | Deerfield River Project and Bear Swamp Project Hydro Coordination Agreement | Land - 17,707 Water - 4,256 | 84 cfs | Jan - 152 Feb - 148 Mar - 87 Apr - 55 May - 112 Jun - 78 Jul - 40 Aug - 68 Sep - 60 Oct - 44 Nov - 71 Dec - 89 | Above - N/A Below - USGS 01168500 Charlemont, MA RM 24.5 | 30 | 2 | ZoE 1 - RM 71.6 to 66 ZoE 2 - RM 66 to 61.2 | ZoE 1 - Impoundment ZoE 2 - Downstream Reach | ZoE 1 - Somerset Impoundment to Somerset Dam ZoE 2 - Somerset Dam to Seasrsburg Impoundment
Searsburg | Deerfield | Searsburg, Windham, VT | 60.3 | 42°54'7.34"N | 72°56'59.88"W | 1922 | 5 | 17685 | Peaking and daily storage | Unit 1 - Vertical Francis - 5 MW | 35 | 365 | 1.18" | No major equipment upgrades have taken place since the previous LIHI submittal | No major operational changes have taken place since the previous LIHI submittal | No facility upgrades or license amendments are planned | 1922 | 50' + 5' flashboards | 1749.66' - 13,700 cfs at 1459.66' | Dam - 1730' to 1733' Powerhouse - 1520' to 1524' | Wooden stave - 18,412' Steel penstock - 495' | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | May 1 to Oct 31: 1746.6' - 1754.6' Nov 1 to Apr 30: 1746.6' - 1749.6' | May 1 to Oct 31: 1746.6' - 1754.6' Nov 1 to Apr 30: 1746.6' - 1749.6' | 412 AF 30 AC | 197 AF 16 AC | Jun 1 to Sep 30: Minimum flow - 35 cfs, or inflow if less Oct 1 to May 31: Minimum flow - 55 cfs, or inflow if less Apr 20 to May 15: Minimum flow - 175 cfs, or inflow if less | Somerset, GRH, 2323, RM 66 | Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 280 cfs | Jan - 324 Feb - 288 Mar - 296 Apr - 562 May - 336 Jun - 238 Jul - 121 Aug - 154 Sep - 173 Oct - 262 Nov - 267 Dec - 342 | Above - N/A Below - USGS 01168500 Charlemont, MA RM 24.5 | 90 | 3 | ZoE 3 - RM 61.2 to 60.3 ZoE 4 - RM 60.3 to 56.8 ZoE 5 - RM 56.8 to 55.7 | ZoE 3 - Impoundment ZoE 4 - Bypassed Reach ZoE 5 - Downstream Reach | ZoE 3 - Seasrsburg Impoundment to Searsburg Dam ZoE 4 - Searsburg Dam to Seasrsburg Powerhouse ZoE 5 - Searsburg Powerhouse to Harriman Impoundment | A1 Aquaitic Biota Aquatic Habitat Fishing B2 Swimming Boating Aesthetic Public Water Source Irrigation
Harriman | Deerfield | Whitingham, Windham, VT | 48.5 | 42°47'36.28"N | 72°54'53.99"W | 1924 | 41 | 99605 | Peaking and seasonal storage | Unit 1 - Vertical Francis - 13.7 MW Unit 2 - Vertical Francis - 13.7 MW Unit 3 - Vertical Francis - 13.7 MW | 288 per unit 864 total | 533 per unit 1,599 total | 1.93" | No major equipment upgrades have taken place since the previous LIHI submittal | No major operational changes have taken place since the previous LIHI submittal | No facility upgrades or license amendments are planned | 1924 | 215.5' + 2.5' parapet wall | 1491.66' - 27,520 cfs at 1499.66' | Dam - 1303' to 1306' Powerhouse - 1101' to 1110' | Concrete conduit - 12,812' Steel penstock - 620' | No major infrastructure changes have taken place since the previous LIHI submittal | Storage/Power | Deerfield River | Deerfield River | N/A | Apr 1 to Nov 1: 1475' maximum summer/fall drawdown Nov 2 to Mar 31: 1440' maximum annual drawdown | Summer: 1483' - 1491' Winter: 1440' - 1491' | 117,300 AF 2,039 AC | 103,375 AF 1,796 AC | Oct 1 to Jun 30: Minimum flow - 70 cfs Jul 1 to Sept 30: Minimum flow - 57 cfs Apr 1 to Jun 15: Rising or stable when flows are within the licensee' s control Jun 16 to Jul 15: Maximum drawdown rate of 1' per day | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 | Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 505 cfs | Jan - 799 Feb - 770 Mar - 627 Apr - 577 May - 428 Jun - 405 Jul - 306 Aug - 387 Sep - 338 Oct - 342 Nov - 438 Dec - 639 | Above - N/A Below - USGS 01168500 Charlemont, MA RM 24.5 | Gross - 184 Net Below Somerset - 154 | 3 | ZoE 6 - RM 55.7 to 48.5 ZoE 7 - RM 48.5 to 44.1 ZoE 8 - RM 44.1 (~430 ft) | ZoE 6 - Impoundment ZoE 7 - Bypassed Reach ZoE 8 - Tailrace | ZoE 6 - Harriman Impoundment to Harriman Dam ZoE 7 - Harriman Dam to Harriman Powerhouse ZoE 8 - Harriman Powerhouse to Sherman Impoundment
Sherman | Deerfield | Rowe, Franklin, MA | 42 | 42°43'46.84"N | 72°55'49.20"W | 1927 | 6 | 28596 | Peaking and weekly storage | Unit 1 - Vertical Francis - 6 MW | 380 | 456 | 2.18" | No major equipment upgrades have taken place since the previous LIHI submittal | No major operational changes have taken place since the previous LIHI submittal | No facility upgrades or license amendments are planned | 1927 | 110' + 4' flashboards | 1103.66' - 23,940 cfs at 1113.66' | 1026' - 1019' | Concrete conduit - 98' Steel penstock - 227' | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | No authorized limits. | 1103.66' - 1107.66' | 3,593 AF 218 AC | 1,359 AF 135 AC | NA | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 | Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 743 cfs | Jan - 1,059 Feb - 960 Mar - 938 Apr - 1,127 May - 688 Jun - 598 Jul - 407 Aug - 511 Sep - 485 Oct - 536 Nov - 661 Dec - 941 | Above - N/A Below - USGS 01168500 Charlemont, MA RM 24.5 | 216 | 2 | ZoE 9 - RM 44.1 to 42 ZoE 10 - RM 42 to 38.5 | ZoE 9 - Impoundment ZoE 10 - Tailrace, Impoundment, Canal System | ZoE 9 - Sherman Impoundment to Sherman Dam ZoE10 - Sherman Dam to D5 Dam and D5 Powerhouse
Deerfield No. 5 | Deerfield | Rowe, Franklin, MA | 41.2 | 42°43'20.94"N | 72°56'19.42"W | D5 - 1974 Dunbar - 1914 | 14 | 53534 | Peaking and daily storage | Unit 1 - Vertical Francis - 14 MW | 637 | 1176 | 3.09" | No major equipment upgrades have taken place since the previous LIHI submittal | No major operational changes have taken place since the previous LIHI submittal | D5 - License amendment for installation of a minimum flow unit was issued on January 5, 2016. The turbine generator is scheduled for installation Sept 2021. | Dunbar rebuilt in 1991 | 35' + 8' steel gates | 1018.66' - 11,662 cfs at 1028.66' | Dam - 995' to 998' Powerhouse - 830' to 870' | Canals - 10,210' Concrete conduits - 3,367' Tunnels - 1,361' Steel penstock - 400' Dunbar Brook, above diversion - pool 500' in length; Dunbar Brook-, below diversion - 1000' in total, with 250' inside road crossing culvert and lower portion affected by bypass flow. | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | No authorized limits. | 1022.66' - 1026.66' | 118 AF 38 AC | minimal usable storage, no surface area calc. Elevations within the Development's small impoundment, three canals and Dunbar Brook above diversion will fluctuate approximately 1-2 feet but not as impoundment storage - more akin to oscillation within the system | Minimum flow - 73 cfs or inflow, whicever is less, but not less than 57 cfs | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 | Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 728 cfs | Jan - 1,034 Feb - 964 Mar - 878 Apr - 1,054 May - 679 Jun - 575 Jul - 435 Aug - 525 Sep - 500 Oct - 527 Nov - 650 Dec - 911 | Above - N/A Below - USGS 01168500 Charlemont, MA RM 24.5 | Dam - 237 Powerhouse - 248 | D5 - 2 Dunbar - 2 | ZoE 11 - RM 41.5 to 38.5 ZoE 12 - RM 38.5 ZoE 13 and 14 - Approximately 1500 ft of the Dunbar Brook where it meets the Deerfield River at approximately RM 40 | ZoE 11 - Bypassed Reach ZoE 12 - Tailrace ZoE 13 - Dunbar Brook, above ZoE 14 - Dunbar Brook, below | ZoE 11 - D5 Dam to Fife Brook Impoundment ZoE 12 - Upper End of Fife Brook Impoundment ZoE 13 - Dunbar Brook above diversion ZoE 14 - Diversion Structure below diversion | Class B Cold Water - from state line to North River (D4 Bypassed Reach) Warm Water - from North River to Connecticut River
Deerfield No. 4 | Deerfield | Buckland, Franklin, MA | 20 | 42°37'12.13"N | 72°44'42.64"W | 1912 | 6 | 15876 | Peaking and daily storage | Unit 1 - Horizontal Francis - 2 MW Unit 2 - Horizontal Francis - 2 MW Unit 3 - Horizontal Francis - 2 MW | 75 per unit 225 total | 480 per unit 1,400 total | 2.0" | No major equipment upgrades have taken place since the previous LIHI submittal | No major operational changes have taken place since the previous LIHI submittal | March 24, 2016 FERC order suspended license articles requiring downstream fish passage. | 1912 | 50' + 4' flashboards | 465.66' - 30,830 cfs at 466.66' | Dam - Powerhouse - | Concrete conduit - 1,514' Steel penstock - 154' | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | No authorized limits. | 465.66' - 469.66' | 467 AF 75 AC | 432 AF 69 AC | Oct 1 to May 31: Minimum flow - 100 cfs, or inflow Jun 1 to Sep 30: Minimum flow - 125 cfs, or inflow | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 | Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 1155 cfs | Jan - 1,516 Feb - 1,487 Mar - 1,566 Apr - 1,799 May - 1,081 Jun - 925 Jul - 564 Aug - 698 Sep - 830 Oct - 881 Nov - 1,046 Dec - 1,471 | Above - USGS 01168500 Charlemont, MA RM 24.5 Below - USGS 01170000 West Deerfield, MA RM 9.0 | 404 | 3 | ZoE 15 - RM 23 to 20 ZoE 16 - RM 20 to 18.5 ZoE 17 - RM 18.5 | ZoE 15 - Impoundment ZoE 16 - Bypassed Reach ZoE 17 - Tailrace | ZoE 15 - D4 Impoundment to D4 Dam ZoE 16 - D4 Dam to D3 Impoundment ZoE 17 - D4 Powerhouse
Deerfield No. 3 | Deerfield | Buckland, Franklin, MA | 17 | 42°36'7.59"N | 72°44'21.82" | 1912 | 7 | 25239 | Peaking and daily storage | Unit 1 - Horizontal Francis -2.3 MW Unit 2 - Horizontal Francis - 2.3 MW Unit 3 - Horizontal Francis - 2.3 MW | 75 per unit 225 total | 480 per unit 1,400 total | Original - 1" Revised - 2.5" | No major equipment upgrades have taken place since the previous LIHI submittal | Removeal of rack overlays for downstream smolt passage, March 24, 2016. | March 24, 2016 FERC order suspended license articles requiring downstream fish passage. | 1912 | 15' + 6' flashboards | 396.66' - 60,805 at 406.66' | Dam - 381' to 384' Powerhouse - 333' to 336' | Concrete conduit - 677' Canal - 880' Steel penstock - 159' | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | No authorized limits. | 396.66' - 402.66' | 221 AF 42 AC | 200 AF 38 AC | Minimum flow - 100 cfs or inflow | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 | Gardner Falls, Central Rivers Power, 2234, RM 15.8 Deerfield No. 2, GRH, 2323, RM 13.2. |  |  | 1,268 cfs | Jan - 1,644 Feb - 1,485 Mar - 1,812 Apr - 2,176 May - 1,158 Jun - 1,009 Jul - 599 Aug - 707 Sep - 888 Oct - 1,013 Nov - 1,092 Dec - 1,635 | Above - USGS 01168500 Charlemont, MA RM 24.5 Below - USGS 01170000 West Deerfield, MA RM 9.2 | 500 | 3 | ZoE 18 - RM 18.5 to 17 ZoE 19 - RM 17 to 16.8 ZoE 20 - RM 16.8 | ZoE 18 - Impoundment ZoE 19 - Bypassed Reach ZoE 20 - Tailrace | ZoE 18 - D4 Powerhouse to D3 Dam ZoE 19 - D3 Dam to D3 Powerhouse ZoE 20 - D3 Powerhouse
Deerfield No. 2 | Deerfield | Conway, Franklin, MA | 13.2 | 42°34'23.63"N | 72°42'23.55"W | 1913 | 7 | 19740 | Peaking and daily storage | Unit 1 - Horizontal Francis -2.3 MW Unit 2 - Horizontal Francis - 2.3 MW Unit 3 - Horizontal Francis - 2.3 MW | 144 per unit 432 total | 513 per unit 1,539 total | 2.0" | No major equipment upgrades have taken place since the previous LIHI submittal | June 2018, the skimmer gate was automated for remote operation. | June 22, 2015 FERC order suspended license articles requiring upstream fish passage. March 24, 2016 FERC order suspended license articles requiring downstream fish passage. | 1913 | 70' + 10' flashboards + 10' inflatable dam | 284.66' - 14,848 cfs at 293.96' | 225' - 232' | Steel penstock - 35' | No major infrastructure changes have taken place since the previous LIHI submittal | Power | Deerfield River | Deerfield River | N/A | No authorized limits. | 284.66' - 294.66' | 550 AF 63.5 AC | 500 AF 57 AC | Minimum flow - 200 cfs | Somerset, GRH, 2323, RM 66 Searsburg, GRH, 2323, RM 60.3 Harriman, GRH, 2323, RM 48.5 Sherman, GRH, 2323, RM 42 Deerfield No. 5, GRH, 2323, RM 41.2 Fife Brook, Brookfield, 2669, RM 36.5 Deerfield No. 4, GRH, 2323, RM 20 Deerfield No. 3, GRH, 2323, RM 17 Gardner Falls, Central Rivers Power, 2234, RM 15.8 | N/A |  |  | 1,478 cfs | Jan - 1,868 Feb - 1,765 Mar - 2,115 Apr - 2,384 May - 1,322 Jun - 1,214 Jul - 758 Aug - 894 Sep - 1,057 Oct - 1,110 Nov - 1,315 Dec - 1,935 | Above - USGS 01168500 Charlemont, MA RM 24.5 Below - USGS 01170000 West Deerfield, MA RM 9.2 | 508 | 2 | ZoE 21 - RM 14.7 to 13.2 ZoE 22 - RM 13.2 to 7.3 | ZoE 21 - Impoundment ZoE 22 - Downstream Reach | ZoE 21 - D2 Impoundment to D2 Dam ZoE 22 - D2 Dam to Unregulated Reach
[7 empty] | 86 | 260275